## MASTER PM MATRIX
GA10 DATA CENTER — MASTER PREVENTIVE & ROUTINE MAINTENANCE MATRIX
Frequency of routine tasks per equipment. ● = routine task exists at that interval. Detail on each equipment tab. Source: GA10 SOP Library v11
Equipment / System | Shift/Daily | Weekly | Monthly | Quarterly | Semi-Annual | Annual | Multi-Yr | Event/As-Needed
UPS — Toshiba 3000TP | ● |  | ● | ● |  | ● | ● 5-yr
UPS Battery (VRLA/Li-ion) |  |  | ● |  | ● |  | ● 5-yr
Standby Generator | ● (run wk n/a) |  | ● no-load | ● loaded |  |  |  | ● fueling
Chiller — YORK YVAA | ● | ● | ● | ● | ● | ●
Chilled Water System | ● | ● | ● | ● | ● | ● |  | ● strainers
Switchgear / Breakers | [7 empty] | ● per movement
Grounding System | [5 empty] | ●
Power Quality / Harmonics |  |  | ●
EPMS / BMS Alarms | ● | [6 empty] | ● per alarm
Fire Detection & Suppression | ● rounds |  | ● |  |  |  |  | ● impairment
Roof / Envelope / Grounds |  |  | ● |  |  |  |  | ● post-weather
Controls / Firmware | [5 empty] | ● |  | ● per change

## UPS - Toshiba 3000TP
UPS UNIT — Toshiba 3000TP (80 kW / 80 kVA, 480 V, 60 Hz)
Preventive & routine maintenance schedule ¦ Source: SOP 40.2001 + SOP 30.XXXX (Battery)
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Per shift | Verify UPS ID/tag vs round sheet; inspect enclosure for damage, unusual sound/odor | Correct asset ID; no abnormalities | SOP 40.2001 §8
Per shift | Verify HMI shows Online / Load-on-Inverter; both power modules Ready (green) | Green steady; N+1 healthy | SOP 40.2001 §8
Per shift | Record input voltage (3-ph), output voltage, load %, module load balance | In ~480 V ±5%; out ±2%; load ≤80%; modules balanced ±5% | SOP 40.2001 §8
Per shift | Record battery voltage, charger status, battery temperature | Float V per spec; ambient ≤25 °C | SOP 40.2001 §8
Per shift | Confirm RemotEye telemetry current on BMS; verify room temp & humidity | No stale data; 64–80 °F, RH 40–60% | SOP 40.2001 §8
Daily | HMI status check, LED verification, load/voltage log | No unresolved alarms | SOP 40.2001 §14
Monthly | Thermal scan of terminations; filter visual inspection; battery temp survey | No hot spots; filters clean | SOP 40.2001 §14
Monthly | Record frequency, power factor, intake air temp; verify fans & filters | 60 Hz ±0.5; intake ≤104 °F; fans OK | SOP 30.XXXX Battery
Monthly | Pull last 30-day event log (HMI/SNMP); verify no unresolved critical alarms | No unresolved critical alarms | SOP 30.XXXX Battery
Monthly | Verify static bypass ready; manual maintenance bypass labeled/accessible; LOTO points labeled | Ready/green; present & labeled | SOP 30.XXXX Battery
Monthly | Verify SNMP/NMC to DCIM; critical alarms mapped to NOC; ≥12-mo data retention | Poll <60 s stale; test ack; ≥12 mo | SOP 30.XXXX Battery
Quarterly | RemotEye communications test; waveform capture review; PCB age query | Comms OK | SOP 40.2001 §14
Annual | Full Toshiba-authorized PM (torque, capacitor, firmware review); SOP document review (July) | Per Toshiba spec (vendor MOP) | SOP 40.2001 §14
5-Year | Capacitor replacement per Toshiba bulletin | Comprehensive vendor MOP | SOP 40.2001 §14

## UPS Battery
UPS BATTERY SYSTEM — VRLA & Li-ion cabinets (supports Toshiba 3000TP)
Monthly procedure (45–60 min) unless noted ¦ Source: SOP 30.XXXX Battery Monitoring & Inspection
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Monthly | Inspect cabinets/racks for corrosion, leakage, swelling, dents, discoloration | No abnormalities | SOP 30.XXXX
Monthly | Inspect inter-cell/inter-tier connections; torque marks intact, no heat discoloration | Torque marks intact | SOP 30.XXXX
Monthly | Verify ventilation; IR thermal scan cell-to-cell ΔT | VRLA H₂ <1% LEL, ΔT <5 °F; Li-ion ΔT <5 °C | SOP 30.XXXX
Monthly | Verify disconnects/OCPD labeled-closed-accessible; PPE, signage, Class-D extinguisher (Li-ion) | Labeled; extinguisher within 25 ft | SOP 30.XXXX
Monthly | VRLA: record string float V, high/low cell V, ΔV vs avg | Float ±1% spec; flag ΔV > ±0.05 V | SOP 30.XXXX
Monthly | VRLA: impedance/conductance vs baseline; charger current; ambient temp; runtime | Flag >20% deviation from baseline; runtime ≥ design | SOP 30.XXXX
Monthly | Li-ion (via BMS): SOC, SOH, module/cell V spread, cell temp spread | SOC 90–100%; SOH ≥80%; module ≤50 mV; cell ≤25 mV; ΔT ≤5 °C | SOP 30.XXXX
Monthly | Li-ion: isolation resistance pack-to-ground; active BMS faults; firmware version | Isolation >500 Ω/V; record faults/firmware | SOP 30.XXXX
Semi-Annual | Battery impedance / ohmic test (vendor MOP) | Compare to baseline; >20% = flag | SOP 30.XXXX
5-Year | Battery replacement per Toshiba bulletin | Comprehensive vendor MOP | SOP 40.2001 §14

## Generator
STANDBY / DIESEL GENERATOR(S)
Test & PM schedule ¦ Source: SOP 30.XXXX Monthly No-Load, SOP 30.2003 Quarterly Loaded Run, SOP Fueling
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Monthly | No-load confidence run — 15 min at no load; initiate Fire System Impairment first; OCC comms | Starts, runs clean; return switch to AUTO | SOP 30.XXXX No-Load
Monthly | During run: inspect exhaust (leaks/color), walk-around, check for noises/alarms, coolant sight glasses, fuel/oil/coolant leaks | Clear exhaust; no leaks; no abnormal alarms | SOP 30.XXXX No-Load
Monthly | Record fuel %, oil %, coolant/oil/exhaust temp, engine hrs, battery V, torque %, fuel rate, fuel & oil psi | Values logged for trending | SOP 30.XXXX No-Load
Quarterly | Loaded run — 1 hr on building load (transfer via System Control Switch to ONLINE at AASB); 5-min cooldown; return to AUTO | Gen reaches rated V/speed, synchronizes, breaker closes | SOP 30.2003
Quarterly | Verify each gen synchronizes; TCC breaker Closed during / Open after; verify UPS operates properly | Correct transfer sequence; UPS OK | SOP 30.2003
Quarterly | Record AC V (ph-ph), amps/phase, Hz, kW, load %, RPM, DEF level/temp, fuel/oil/coolant/exhaust temps, biases, pressures | Values logged for trending | SOP 30.2003
Before/After every run | Generator Pre-Run, Running, and Post-Run Checks | Per SOP 30.2001 | SOP 30.2001
As needed (fuel level) | Refueling — verify ABC extinguishers, spill kits, truck brakes/chocks, bond truck to enclosure | Safety items staged; truck grounded | SOP Fueling
As needed (fuel level) | Record bulk-tank level (gal & %) before/after; monitor continuously; pump slowly; inspect hoses/connections | Do not overfill; no leakage; spill → Hazmat EOP | SOP Fueling

## Chiller - YORK YVAA
YORK YVAA AIR-COOLED CHILLER (CH-1…CH-10, R-513A, 500 tons)
PM schedule ¦ Source: SOP-011 YORK YVAA ¦ Normal: CHWS 55°F, CHWR 70°F, 845 GPM, 460 V
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Daily | Operator rounds: visual for oil/refrigerant/water leaks, vibration, noise, loose panels, coil fouling | Document abnormalities; escalate if CHWS >60 °F or capacity loss >25% | SOP-011
Daily | BAS verification: availability, AUTO mode, no critical alarms, correct lead/lag; acknowledge alarms | AUTO; no active critical alarms | SOP-011
Daily | Record evap entering/leaving water temp & pressure & flow; compressor suction/discharge/oil pressure, discharge temp, VFD speed; condenser fan status, ambient, head pressure | CHWS 55°F; CHWR 70°F; flow 845 GPM | SOP-011
Weekly | Record operating data; check alarms; verify fan operation | Fans operating | SOP-011
Monthly | Clean coils; inspect electrical connections; review VFD history | Coils clean; connections tight | SOP-011
Quarterly | Vibration analysis; inspect contactors; inspect terminal lugs | Within vibration limits; no pitting | SOP-011
Semi-Annual | Verify sensors; test flow switches; confirm BAS integration | Sensors accurate; flow proof works | SOP-011
Annual | Refrigerant leak survey; oil analysis; electrical testing; safety-device testing; vendor inspection | No leaks; oil in-spec; vendor sign-off | SOP-011

## Chilled Water System
GA10 CHILLED WATER DISTRIBUTION SYSTEM (pumps, VFDs, valves, TES, sensors)
PM schedule ¦ Source: SOP-GA10-CHW Rev 2.3 ¦ PCHWS target 55°F; TES = 2×15,000 gal in series
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Each shift / ≤4 hr | Review & record: active alarms/overrides, SCHWS/PCHWS temps, loop ΔP, pump/VFD status, TES tank temps, Ignition comms | No unack critical alarms; temps/ΔP stable; no unauthorized overrides | SOP-GA10-CHW
Each shift / ≤4 hr | Log PCHWS (55°F), PCHWR/SCHWR trend, SCHWS, loop ΔP, VFD speed, Belimo valve comms, condensation sensor, cold-deck supply air temp | Within site-approved bands; BACnet online; dry | SOP-GA10-CHW
Weekly | Inspect visible piping, valve bodies/actuators, insulation, strainers, pump seals, VFD panels, control enclosures | No leaks, condensation, actuator faults, corrosion, abnormal vibration | SOP-GA10-CHW
Monthly | Review Ignition trends, alarm history, overrides, comm dropouts, ΔT, pump-speed & valve-demand patterns | Trends match load; no saturated valve demand or drift | SOP-GA10-CHW
Monthly | Inspect TES stratification, top/bottom temp trends, air vents, vacuum breakers, manways, isolation valves | Stratification stable; no mixing/leakage/vent obstruction | SOP-GA10-CHW
Quarterly | Comms check: BACnet/IP, Modbus RTU, DDC switch, KMC controllers, Belimo valves, Ignition supervisory | All critical devices online; no stale data / duplicate addr | SOP-GA10-CHW
Quarterly | Test selected alarms & point responses (chiller/pump/VFD fault, high SCHWS, low ΔP, condensation, controller offline, TES runtime) | Priority, routing, proof-delay, logging per approved | SOP-GA10-CHW
Semiannual | Calibrate/validate critical sensors (PCHWS/R, SCHWS/R, supply/return air, humidity, condensation, ΔP, TES temps) | Within tolerance vs calibrated reference; fail → repair/replace | SOP-GA10-CHW
Semiannual | Stroke CHW & TES valves through commanded positions; verify feedback, travel, fail position, comms | Command/feedback align; closes off; no binding | SOP-GA10-CHW
Annual | Inspect pumps, VFDs, starters, panels, strainers, isolation/bypass valves, expansion tank, mechanical supports | Clean, secure, labeled, accessible; no abnormal heat/vibration | SOP-GA10-CHW
Annual | Review controller programs, graphics, point mapping, setpoints, alarm thresholds, backups, user access, change history | Docs match field; backups current; changes traceable | SOP-GA10-CHW
As needed | Clean strainers after startup, major maintenance, pump/valve replacement, water-treatment upset, or debris event | Strainers free of restricting debris | SOP-GA10-CHW
Per vendor | Chilled-water sampling & treatment: pH, inhibitor, corrosion, biological, conductivity, discharge params | Chemistry within vendor-approved limits | SOP-GA10-CHW

## Switchgear-Breakers
SWITCHGEAR / CIRCUIT BREAKERS
On-demand controlled procedure (not calendar PM) — ~2 hr/event ¦ Source: SOP 30.0006 Rack-In/Rack-Out
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Per event | Verify breaker & cubicle ID vs labels/one-line + independent peer verification | Stop if any ID/doc mismatch | SOP 30.0006
Per event | Confirm personnel qualifications, roles, comms, stop-work authority, hold points at pre-task brief | Qualified personnel & authorities confirmed | SOP 30.0006
Per event | Verify PPE, barricades, arc-flash boundary, remote racking tools, test equipment serviceable | Arc-flash PPE per current label/study | SOP 30.0006
Per event | Verify LOTO, switching, isolation, absence-of-voltage per approved plan | Requirements satisfied within scope | SOP 30.0006
Per event | Pre-movement inspection of breaker/cubicle external condition; record initial state & EPMS/BMS indications | No damage, contamination, overheating, water intrusion; indications expected | SOP 30.0006
Per event | Perform rack-in / rack-out per OEM + approved MOP/switching order | No interlock bypass; stop on binding/alarm/flash/smoke/odor | SOP 30.0006
Per event | Verify final position (mechanical + electrical + EPMS/BMS + peer); confirm no unexpected alarms/trips | Final position matches intent; no abnormal indications | SOP 30.0006
Per event | Restore covers/ports, housekeeping; document initial/final state, personnel, alarms, photos, deficiencies | Complete work-order record | SOP 30.0006

## Grounding System
GROUNDING & BONDING SYSTEM
Annual visual-only inspection (~2 hr) — no testing/disconnecting ¦ Source: SOP 30.0007
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Annual | Inspect main ground bus bars & grounding electrode conductor connection points (visible) | Secure, labeled, no severe corrosion/damage | SOP 30.0007
Annual | Inspect elec rooms, switchgear, UPS/battery rooms, gen yard, service entrance bonding jumpers/lugs/enclosures | No missing/loose/damaged/corroded/unmarked bonding | SOP 30.0007
Annual | Inspect data-hall racks, cabinets, ladder rack/cable tray, overhead/underfloor supports, metallic infrastructure | Bonding conductors present, secure, undamaged | SOP 30.0007
Annual | Inspect bonding of metallic piping, supports, fences/gates, fuel-system components, exterior pads, roof curbs | Bonding present/intact where applicable | SOP 30.0007
Annual | Inspect lightning-protection grounding interfaces, down conductors, roof/exterior bonds, labels | No damage, disconnection, missing hardware, corrosion | SOP 30.0007
Annual | Verify ground/bond labels & tags legible; check recent installs/temp equipment for unbonded parts | Legible; no unbonded/dangling conductors | SOP 30.0007
Annual | Look for overheating, arcing, burn marks, mechanical damage, water intrusion, loose hardware, cut conductors | None present; escalate immediately if found | SOP 30.0007

## Power Quality
POWER QUALITY / HARMONICS MONITORING
Monthly data review (~1.5 hr) ¦ Source: SOP 30.0008 ¦ Thresholds per meter config, not numeric in SOP
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Monthly | Review voltage trend data (sag/swell/interruption/transient/imbalance) | No abnormal or repeated deviation vs range | SOP 30.0008
Monthly | Review current trend data (imbalance, loading, neutral current, peak events) | No abnormal change vs prior months | SOP 30.0008
Monthly | Review harmonics — voltage THD, current THD, individual harmonics, PQ distortion alarms | No harmonic alarms / worsening THD trend | SOP 30.0008
Monthly | Review frequency, power factor, demand, kW/kVA/kVAR, crest factor, meter event flags | No abnormal/worsening trends | SOP 30.0008
Monthly | Review event logs — sag/swell/transient, ITIC/CBEMA violations, waveform captures, repeated events by location | No ITIC/CBEMA violations or repeated events | SOP 30.0008
Monthly | Review UPS, switchgear, PDU, RPP, utility/service-entrance monitoring points; compare to prior month | No PQ alarms / comm loss / data gaps; no recurring conditions | SOP 30.0008
Monthly | Document exceptions (screenshots/exports/reports); create corrective WOs; escalate critical findings | Exceptions documented; critical events escalated | SOP 30.0008

## EPMS-BMS Alarms
EPMS / BMS ALARM REVIEW & ACKNOWLEDGMENT
Per-shift review (~0.5 hr) — acknowledge only ¦ Source: SOP 30.0009 + BMS Alarm Mgmt (ATL01-2)
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Per shift | Review active alarm summary; counts by severity/category; include new/repeating/stale/comm-loss/failed-sensor | All active alarms reviewed | SOP 30.0009
Per shift / per alarm | Capture alarm info before ack (name, source, equip/location, timestamp, status, severity); classify by site severity logic | Evidence preserved; each alarm classified | SOP 30.0009
Per shift / per alarm | Acknowledge only after review; validate expected/known/tied-to-work vs needs field verification | No clear/suppress/disable/force/override | SOP 30.0009
Per shift | Electrical alarms: check EPMS for utility, switchgear, UPS, gen, PDU, RPP, breaker, PQ, comms | Related conditions assessed | SOP 30.0009
Per shift | Mechanical alarms: check BMS for chiller, pump, CRAH/CRAC/AHU, liquid cooling, leak, temp/humidity/pressure/flow | Related conditions assessed | SOP 30.0009
Per shift | Document per-alarm actions; create/update corrective WOs; escalate critical; update shift turnover | Critical/life-safety/leak/thermal/redundancy alarms escalated | SOP 30.0009
Per alarm (BMS) | Rapid remote triage within 2–5 min: temp trends (15–30 min), CCU status, CHW supply/return, ΔP, load | CHW ΔP 15–20 PSI; correlate temp+airflow+ΔP+load | BMS ATL01-2
Per alarm (BMS) | Meet severity response times: P1 ≤5 min, P2 ≤15 min, P3 ≤60 min, P4 monitor | Data hall >85°F = P1; field-verify all SEV1/SEV2 | BMS ATL01-2
Ongoing (BMS) | Alarm-quality tuning: eliminate nuisance alarms, tune temp & HAC ΔP thresholds, group related alarms | Reduced alarm flood; track MTTA/MTTR/repeat alarms | BMS ATL01-2
Per event (BMS) | Post-incident review for all SEV1-3 / repeat SEV3 / customer-visible issues | Root cause + corrective/preventive actions documented | BMS ATL01-2

## Fire System
FIRE DETECTION & SUPPRESSION SYSTEM
Inspection rounds (routine) + monthly items ¦ Source: SOP 30.0028 Rounds, SOP 40.XXXX Impairment
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Each round | FACP/releasing panels: readable, powered normally; record Alarm/Trouble/Supervisory/Comm-fault counts | No alarm/trouble/supervisory/ground/power/comm fault | SOP 30.0028
Each round | VESDA/aspirating panels normal; inspect sample piping for damage/obstruction/open points; record airflow/filter | Normal status; piping intact | SOP 30.0028
Each round | Sprinkler risers: accessibility, housekeeping, leakage, corrosion, tamper/valve status; record water/system/air PSI | Accessible; no leakage; low/zero pressure escalated | SOP 30.0028
Each round | Control valves in normal position, locked/sealed/tagged, accessible | Normal + sealed; any closed/unsealed escalated | SOP 30.0028
Each round | Fire pump room: controller status, leaks, standing water, alarms; record suction/discharge/jockey PSI | Normal; fire pump unavailable escalated immediately | SOP 30.0028
Each round | Clean-agent/water-mist cylinders & panels: securement, discharge indicators, pins/seals, gauges | Secured; no discharge; gauges normal | SOP 30.0028
Each round | Data halls: no blocked heads/detectors/pull stations/FDC/egress; no coverage gaps from tiles/panels | Clear coverage & clearances | SOP 30.0028
Monthly | FDC exterior: clear access, caps, signage, threads, condition | Clear & acceptable | SOP 30.0028
Monthly | Fire pump run (requires Fire System Impairment) | Pump runs per test; impairment cancelled after | SOP 40.XXXX
During impairment | Inspect affected area at least hourly until impairment cancelled; on restoration verify 'All Systems Normal' vs baseline | No new alerts vs pre-impairment baseline | SOP 40.XXXX

## Roof-Envelope-Grounds
ROOF, ENVELOPE & SITE GROUNDS
Monthly rounds or post-weather walkdown (~0.5 hr) ¦ Source: SOP 30.0029
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Monthly / post-weather | Roof surface: no ponding, membrane damage, open seams, loose material/ballast/debris | No defect observed | SOP 30.0029
Monthly / post-weather | Roof drainage: drains/scuppers/gutters/downspouts/overflow clear; no erosion or abnormal discharge | Drainage clear | SOP 30.0029
Monthly / post-weather | Roof equipment/penetrations: flashing, sealants, curbs, pipe supports intact; conduit sealed; lightning protection intact | Intact & sealed | SOP 30.0029
Monthly / post-weather | Building envelope: walls, panels, louvers, doors, windows, seals; no cracks/spalling/staining/intrusion | No visible defects | SOP 30.0029
Monthly / post-weather | Stormwater: catch basins, trench drains, swales, culverts, low points unobstructed; no standing water/erosion | Unobstructed; no flooding | SOP 30.0029
Monthly / post-weather | Site grounds/pavement: sidewalks, roads, parking free of potholes, trip hazards, debris, blocked emergency access | Clear & safe | SOP 30.0029
Monthly / post-weather | Generator/utility yard: fencing, gates, bollards, fuel-fill, utility entrances secure; no fuel/oil staining or leakage | Secure; no staining/leakage | SOP 30.0029
Monthly / post-weather | Exterior security: perimeter fence, gates, doors, cameras, lighting, bollards intact & unobstructed | No breach or blocked device | SOP 30.0029
Post-weather | Severe-weather assessment: wind damage, shifted roofing, fallen limbs, utility impact, flooding, structural/water intrusion | No damage identified | SOP 30.0029

## Controls-Firmware
CONTROLS / FIRMWARE MANAGEMENT (BAS, UPS, PDU, switchgear, PLC, chiller, CRAH)
Change-triggered validation + tiered soak ¦ Source: Firmware Validation SOP GA10-FW-VAL-001
Frequency | Task / Activity | Acceptance Criteria / Reference Value | Source SOP
Per change (pre) | Confirm approved window, change record, rollback plan, OEM contact, Ops comms path, redundancy available | All 6 confirmed before work | GA10-FW-VAL-001
Per change | Step 1 Firmware: correct version installed, reboot successful, no install errors | Version matches approved; no errors | GA10-FW-VAL-001
Per change | Step 2 Device health: hardware/controller/fan/power/temperature | No new faults, warnings, degraded states | GA10-FW-VAL-001
Per change | Step 3 Monitoring: visible in DCIM & EPMS/BMS; telemetry & logging operational | Current & accurate status displayed | GA10-FW-VAL-001
Per change | Step 4 Alarms: no unexpected critical alarms/warnings; notifications functioning | No unexplained alarms | GA10-FW-VAL-001
Per change | Step 5 Functional: system & customer services operational, config retained, comms normal | No service impact | GA10-FW-VAL-001
Per change | Step 6 Redundancy: N/N+1 available, cluster healthy, HA/failover operational | No loss of resiliency | GA10-FW-VAL-001
Per change | Step 7 Security: authentication, MFA, RBAC, logging operational | Security controls normal | GA10-FW-VAL-001
Post-change soak | Monitor new alarms/log errors/perf degradation/comm issues/restarts — Tier1 24h, Tier2 72h, Tier3 7d, Tier4 14d | Close only after soak complete, no unresolved conditions, approvals obtained | GA10-FW-VAL-001
Annual | Firmware SOP document review (or after major incident) | Reviewed / updated | GA10-FW-VAL-001